Details of values that can be set by MENU button for v1.0 Solar Controller software

| No | Variable | Default (Note 3) | Range (Note 2) | Units | Notes |
| --- | --- | --- | --- | --- | --- |
| 0. | Normal Display | 0 | 0-1 |  | Normal or maintenance display. Change to 1 after initial testing |
|  | DST | 0 | -12 to +12 | Hours | To correct for Daylight Saving Time and large longitude errors |
|  | Minute_offset | -10 | -59 - +59 | minute | To correct for longitude and annual time errors |
|  | HWC_set_temp | 60 | 30-80 | C | HWC set temperature for heating by solar in absolute mode |
|  | Diff_Mode | 1 | 0-1 |  | Differential or absolute mode |
|  | Diff_set | 3 | 0-10 | C | Differential between Panel and HWC bottom sensor. Pump triggered after this value exceeded. |
|  | Panel_voltage | 120 | 50-500 Note 1 | dV | Set to 60 or 120 only. Can not process any other numbers in early software versions |
|  | Backup_heat_hour | 19 | 12-23 | hour | Time when backup comes on |
|  | Backup_heat_temp | 55 | 30-80 | C | HWC set temperature for heating by boiler, etc. |
|  | Backup_heat_economy_mode | 1 | 0-1 |  | Sets forward prediction of tomorrow’s likely solar input |
|  | Backup_heat_economy_reduction | 10 | 0-50 | C | Reduction in temperature made when above is set |
|  | Aux_temp | 4 | -30 - +125 | C | Set point for aux channel |
|  | Aux_hysteristis | 2 | 0-10 | C | Hysteresis for aux channel |
|  | Aux_alarm_on_rising | 0 | 0-1 |  | If 1, buzzer and relay activate when alarm thresholds exceeded. Generally use falling for controlling heaters and rising for coolers. |
|  | Aux_buzzer_threshold | 2 | 0-10 | C | Added to Aux _temp, buzzer comes on when it’s exceeded so that it switches relay first then triggers buzzer if still rising. (or subtracted fro a switching on falling temperature. ) |
|  | Temp_scaler1 | 100 | 1-255 |  | Calibration of temperature sensor |
|  | Temp_scaler2 | 100 | 1-255 |  | Temperature = ( ( A/D 10 bit reading / 4 ) * Temp_scaler1 + 50 ) / ( 408 / 4 ) - 50 |
|  | Temp_scaler3 | 100 | 1-255 |  |  |
|  | Temp_scaler4 | 100 | 1-255 |  |  |
|  | Temp_scaler5 | 100 | 1-255 |  |  |
|  | PV_scaler | 43 |  |  | PV_voltage = PV_reading * 10 / (PV_scaler+1) |
|  | Dw_scaler (in Decawatt) | 225 |  |  | Based on flow rate at max voltage in litres per minutes-1 Dwatt_av_for_60mins = ( PV_av_vshort - Pump_on_threshold ) * ( T11 - T14 ) * 10 / ( Dwatt_scaler + 1 ) |
|  | Open_circuit_value | 250 | (1000-1023)/4 |  | Byte value returned when near O/C. Store value /4. Actual value used in programme is Open_circuit_value_real = 4* EEPROM value. |
|  | Short_circuit_value | 40 | 0-40 |  | Byte value returned when near O/C |
|  | Oheat_temp | 85 | 70-90 | C | Max panel temperature experienced in normal use. Only exceeded if system faulty. |
|  | Temp_hysterisis | 1 | 0-9 | C | Temperature hysteresis for pump on/off. Must not be more than Diff_set |
|  | Dawn_light_level | 20 | 5-50 | dV | Suggest you measure the full moon voltage and then daylight on a very dull winter day at mid morning and set the dawn threshold half way between. This is about 2V for a Solartwin panel with integral resistor and 4V if the resistor is removed, both still loaded by the controller. |
|  | Pump_on_threshold = 60 dV | 60 | 10-100 | dV | Pump does not run below this voltage |
|  | Pump_hysterisis = 20 dV | 20 | 0-50 | dV | Voltage hysteresis for pump on/off |
|  | Timing_delay_fine = 190 msec | 150 | 0-250 | msec | Software uses (Timing_delay + 4 x Timing_delay_fine + execution time) =5sec |
|  | Timing_delay | 4 | 3-5 | sec | Ditto |
|  | Time_interrupt | 58 | (500-1500)-850 |  | Interrupt cycles in one minute. Store 850 less than actual value. Programme adds 850 |
|  | Correction_smoothing | 4 | 1-10 |  | Smoothing on daily time correction |
|  | Backup_heat_legionella | 60 | 50-70 | C | Temperature for killing legionella weekly |
|  | Aux_buzzer_on | 1 | 0-1 |  | Aux alarm on |
|  | Buzzer_for_panel | 1 | 0-1 |  | Solar overheat alarm on |
|  | Backup_heat_economy_threshold | 50 | 10-100 | KW | Threshold of total weighted heat for last 8 days above which Backup_heat_economy_mode is possible |
|  | Backup_heat_minutes | 50 | 10-59 | mins | Length of backup heating |

Note 1: Values over 120 dV may overstress the circuit unless some components changed.

Note 2: Range is practical range, not what programme allows. Programme will not warn you if an out of range value is entered.

Note 3: Red is for constants affected by panel voltage. Defaults are for 12V panel. Adjust to suit panel voltage, e.g. halve for a 6V panel.